Technical Note

######

| GSI’s Fast Beam Loss Control System “Schnelle Strahlverlust-Überwachung (SVÜ)” for Unilac, TK and EH – Actual Status and possible Replacements for FAIR | 30.01.2017 |
| --- | --- |
| Authors: M. Schwickert, H. Reeg | Version 0.11 |

This technical note intends to give an actual overview of the existing fast beam loss control system for Unilac, TK and EH at GSI (called “Schnelle Strahlverlustüberwachung (SVÜ)”). A concise overview of the system’s functionalities and performance parameters is presented, as well as the initial requirements that led to the present layout. In addition technical information of all related electronic modules, most of them purpose-built, has been collected, as well as their interfaces to the accelerator control system, the timing system, chopper control etc.

An obvious goal of this document is to serve as a basis for the design of a modernized FBLC system, integrating the operational experience of the GSI accelerator operations team, as well as the future demands of the FAIR accelerator complex. Additionally, the idea of merging the FBLC system with the Makropuls-Selektor (MAPS) is discussed.

Document History

| Version | Prepared by | Checked date | Comment |
| --- | --- | --- | --- |
| V 0.1 | M. Schwickert | 23.04.2017 | First draft |
| V0.11 | H. Reeg, M. Schwickert | 30.06.2017 | Many corrections, supplements by H. Reeg included |

TABLE OF CONTENTS

1	Overview	4

2	Main Requirements of the present SVÜ System	4

2.1	Beam Physics Aspects	5

3	System Layout and Constituents	5

3.1	Installation locations	5

4	Technical Realization	7

4.1	BCT head amplifier	7

4.2	Verlustüberwachungs-Karte FG428.010.000 (SVÜ board)	8

4.2.1	Type SV (beam loss)	10

4.2.2	Type PGS (profile grid protection)	10

4.2.3	Type EMI (emittance measurement grid protection)	10

4.3	SVÜ main frame (Baugruppenträger BGT)	11

4.4	MIL-1553B Interfacekarte FG380.122 / FG380.211	11

4.5	Interlock Status Display	11

4.6	Chopper Control System (CCS)	11

5	Interfaces	12

5.1	Input parameters / set values	12

5.2	Hardware interfaces	12

5.2.1	Hardware interfaces type SV	12

5.2.2	Hardware interfaces type PGS	12

5.2.3	Hardware interfaces type EMI	13

5.3	Software interfaces	13

6	Summary and Evaluation of the SVÜ	13

6.1	Operational experience with FBLC	13

6.2	Service and maintenance aspects	13

7	Future Requirements	14

7.1	Upgrades due to known SVÜ drawbacks	14

7.2	General modernization aspects	14

7.3	Upgrades due to FAIR requirements	14

7.4	Merging with MAPS system?	14

8	Outlook	14

9	Related Documents	14

10	Abbreviations	14

# Overview

The main objective for the installation of the existing SVÜ system at the UNILAC was to prevent activation of or damage to the accelerator by unwanted beam loss during standard machine operation. For this reason an online control system had been designed, manufactured and installed in order to monitor the transmission losses of the ion beam along the UNILAC and towards the transfer channel (Transferkanal TK) or the old experimental hall (EH).

The present SVÜ electronic devices were installed and commissioned until approx. 2006 and are presently only maintained, without any major upgrade since then. Apart from the fact that, in the meantime, many electronic components are outdated, the present SVÜ displays important drawbacks with regard to its robustness, modularity and lack of configurability. In addition, the upcoming FAIR project and the related control system retrofit set up new requirements that demand for a general overhaul of the SVÜ system.

# Main Requirements of the present SVÜ System

The main purpose of the SVÜ system is to monitor beam transmission online and to generate interlock signals on a µs-timescale in case a pre-set threshold for beam loss is crossed.

The source for the online calculation of beam transmission are the beam current measurement data provided by the large number of beam current transformers (BCT) installed in the UNILAC, TK and EH beamlines.

For reference, the associated “Gerätemodell” (device model) DTTC can be found in [4]

Principle of operation

Figure 1 SVÜ Block Diagram

The pulses of the first (upstream) BCT#1 are fed to the up-counting channel of an up/down counter. A second (downstream) BCT#2 is connected to the same counter for down counting of measurement pulses. If during the macro pulse the first BCT generates more counts than the second BCT the counter value increases during the pulse duration. In case the counter value is greater than a pre-set threshold for tolerable beam loss, the SVÜ independently triggers the chopper control system to truncate the present macropulse.

Additional functionalities for profile grids and emittance measurement

In addition to the main task to monitor beam transmission, SVÜ provides functionalities to control a pre-set threshold for the integrated beam current in order to protect a profile grid and/or and emittance measurement setup. Similarly to the beam loss control function, in the latter case the SVÜ directly triggers the chopper control system.

Fundamental SVÜ requirements

- system shall be able to accept many (20+) inputs of BCTs

- for the calculation of transmission/beam loss: locations of adjacent measurement positions (BCT installation location) shall be configurable

- configurable thresholds for max. beam loss between two measurement positions

- generate interlock signals for chopper control

- for “Profilgitter-Schutz”: dynamic truncation of beam pulse in case a pre-set threshold for tolerable beam charge exposed to the grid wires is exceeded

- for “Emittanz-PG-Schutz”: additional threshold value of tolerable beam charge for emittance measurement

## Beam Physics Aspects

- The Unilac macropulse length is 0.01-5 ms. [Comment HR: initially specified to be 8 ms (all diagnostic components should be able to cope with it), but due to some limitations of rf devices this was reduced to 5.5 ms. To be checked.]

Figure 2: Macropulse beam current (from [3]).

TODOs, ideas:

- proper definition of beam current, i.e. ‘integration time’ of counter, needs to be evaluated

- what is the time of flight between adjacent BCTs and is there any influence of the different measurement times in relation to the achieved time resolution?

- BCT calibration, V/f converter

- What is the typical timescale for truncation of the beam pulses?

- time of flight: from sources to TK

# System Layout and Constituents

## Installation locations

Signal sources:

- BCTs installed in UH,..., TK8

Figure 2: BCTs along the UNILAC beam lines

Electronics:

- SVÜ main frames: LSB 4, Rack 14
Inside the bottom 19” main frame the interlock signals are collected and via level adaptors and buffers fed to the chopper control.
In addition, the SVÜ main frame acts as receiver and distribution station for gate and clamp pulses of the BCT system.

- Chopper control system and UNILAC-Pulszentrale: LSB 6, Rack 3

Figure 3: UNILAC BCT and SVÜ channels

# Technical Realization

## BCT head amplifier

Each BCT head amplifier is equipped with a pre-calibrated, fixed-range differential voltage output. These head amplifier signals are connected via a twisted pair cables to the related SVÜ boards.

| Parameter | Value |
| --- | --- |
| Current ranges | 5 ranges: 0.01-0.1-1-10-100 mA full scale (FS) |
| Max. beam current | 40 mA (high resolution version), 100mA (high current version) |
| Output voltage on 15 pin DSub (pins 9 and 10) | +/- 1 V full scale differential, (0.4 V max. in 100 mA range, high res. version) |
| Voltage on LEMO fixed-range output | +/- 1 V full scale differential |
| Overrange margins | ~110% FS positive, ~20% FS negative |
| Monitor output / fixed gain (on LEMOSA 2p socket) | +/- 0.1 V/mA differential, independent of range; 4 V for 40 mA max., positive signal on pin, negative on socket |
| Termination resistor, typical | 680 Ω for both outputs, external |
| Current resolution | 0.5 µA rms / 1 ms pulse duration in range 10 µA 0.5 % FS in other ranges |
| Output voltage rise time | ~1 µs @ small signal, <5 µs @ FS |
| Max. beam pulse length | 5 ms for 1% pulse droop error |
| Gain error | Depending on accuracy of calibration current source |
| Calibration winding | 1 turn via 50 Ω BNC socket, isolated, 1 kΩ series resistor |
| External power supply | Dual 15 +/- 0.4 V DC (pos./neg.) / < 60 mA |
| Logic level for control lines | CMOS 15 V (4000 series, high level>0.5 V+) |

Table 1 BCT electronics specification

- configured for positive particles, which produce a positive output voltage

- active L/R-integrator CT circuit with second order feedback reduces the pulse droop error while preserving working point stability and signal-to-noise ratio

- zero-level clamping technique provides baseline-restoring and noise gating

- range selection and signal clamping controlled via remote lines on 15p-DSub male connector; all inputs pulled down with 4.7 kΩ, all outputs short-circuit-protected

## Verlustüberwachungs-Karte FG428.010.000 (SVÜ board)

Signals of each two consecutive BCTs are fed to two independent V/f-converters on one SVÜ board. On the SVÜ board counter ticks are generated, each representing a fixed amount of beam charge. The actual frequency of these pulses is proportional to the beam current at the position of the related BCT.

The pulses of the first (upstream) BCT are fed to the up-counting channel of an up/down counter. A second (downstream) BCT is connected to the same counter for down counting of measurement ticks. Coincidence of up and down counting pulses is prevented by usage of 180° phase shifted master pulses.

The counter is of signed 13 bit type, thus the measurement range is +/- 18,022 µC.

The configurable resolution of the is set to 2.2 nC beam charge per pulse.

The maximum pulse frequency is 8 MHz, i.e. a time resolution of 125 ns.

Control of beam losses

For the online control of the beam losses the counter value of the up/down counter is permanently compared to a pre-set threshold which defines the maximum allowed charge loss during the macropulse. Each SVÜ board is pre-set with two different set values. Depending on the SVÜ board type, only one of these two set values is actively used.

If the counter exceeds the threshold an interlock signal is generated which is directly fed (hard wired, no CPU etc. involved) into the chopper control of the UNILAC Pulszentrale. This electronic hardware, developed by GSI CSCO (Belab) takes care that the chopper UH2BC1L terminates the actual macropulse. The reaction time for this process is approx. 1 µs.

In order to ensure that measurements with profile grids or BCTs are still possible despite the dynamic beam pulse truncation, the chopper control takes care that the minimum pulse lengths is no shorter than 10 µs.

If the interlock signal is e.g. generated by the last sensor in TK an unavoidable residual charge remains in the accelerator, due to the typical time of flight of 15 µs for a 11.4 MeV/u ion beam, which still can damage the accelerator components.

To ensure that the beam current is only controlled during the macropulse and to reduce offsets, the electronic components require a gate signal defining the selected measurement time interval. In contrast to the BCT digitizers, the SVÜ makes use of the clamp-pulses of the BCT system of the related accelerator sections, as generated by the chopper control in LSB 6.

In addition the SVÜ modules monitor, if prior to the start of the macropulse the thresholds have been set by the SE. In case the thresholds have not been set an interlock signal is generated and in the status register a ‘Sequenzfehler’ is set. This is also done, if thresholds have been pre-set, but no gate pulse occurred in-time.

The control modules provide the following values for the 16bit data bus of the MIL-interface card:

- counter value (= measured charge) after end of gate pulse

- status information of interlock output and ‘Sequenz-Überwachung’

The main part of the digital electronics is implemented in a CPLD (ALTERA MAX7160ELC84). Only the two V/f converter circuits, the bus transceiver and open drain drivers are realized with discrete components.

The yellow LED on the frontpanel (‘SEL’) indicates read/write access.

The red LED (‘INTL’) indicates that an interlock is set.

Figure 4: SVÜ board, type ‚SV‘

Three different types of SVÜ boards exist, see below. All types are equipped with two registers for threshold values, which are both set before each macropulse. It is [Comment HR: locally?] not transparent to the user which of the two registers is actually used as threshold value. Related errors are not easy to detect.

### Type SV (beam loss)

The SVÜ board type SV is the standard version featuring two counter channels and an interlock output on the VG backplane.

Only threshold value ‘1’ is applied, internal or external switching is not foreseen (example: UH3DT2V). These control boards are always active, they react immediately and without any further condition. When the threshold value is exceeded, the macropulse is truncated. For special cases a version with interlock output on the front panel exists, the connection to the sum-interlock tap is not applied in this special version. [Comment HR: to be checked.]

### Type PGS (profile grid protection)

PGS-type boards (example: HT1DT0P) are used to protect the wires of a profile grid located downstream of the measuring BCT#1 from thermal damage. In this case only the UP-input signal is used and routed (via VG backplane) to the next unit, while the DOWN-input is not used (the connections between the down-input and the related UV/f-converter are cut). Thus the absolute beam charge passing the related BCT is monitored, and the already truncated pulse length (100 µs or 250 µs at reduced repetition rate of 2.5 Hz for each accelerator individually) is further dynamically reduced, in order to limit the thermal stress inside the profile grid wires, if necessary.

The interlock signal is routed via a front panel socket and coaxial cable to the chopper control.

Only the second threshold value is evaluated.

Crossing of the threshold value always generates a local interlock in the SVÜ module, but this is only applied to the chopper control for macropulse truncation, if the switch ‘PG-Schutz’ for the related beamline section(s) is set active in the HKR. Only in this case a profile grid may be moved inside the beam path at all.

For the board type PGS the measurement values of the actual ‘beam loss’ can be readout at any time (using NODAL/DTTC). The calculation is done in any case, irrespective of the use case. For the PGS the measurement value represents the absolute charge (not beam loss).

### Type EMI (emittance measurement grid protection)

This SVÜ board type (e.g. TK6DT2E) works similarly to the standard SV board (see 4.2.1). The SVÜ-type EMI is used for the protection of an emittance measurement setup (slit-grid method), especially. If the emittance measurement mode is switched on the active threshold value is changed by the chopper control.

Usually, in between BCT#1 and BCT#2 a slit-pair is installed for the emittance measurement. The profile grid used for the emittance measurement is installed downstream of BCT#2.

In the EMI-type board an additional switch for threshold selection is implemented on the frontpanel, which is triggered by the chopper control, if the related emittance measurement is switched on inside the HKR.

If emittance measurement is switched on by an operator, the up-counter is put out of service and the down-counter is set to up-counting mode. Thus, similar to the profile grid protection (see 4.2.2) an absolute charge measurement is performed and the profile-grid for emittance measurement is protected. In case the emittance measurement for a given section is switched on, the beam loss control (SVÜ) function is set inoperative.

## SVÜ main frame (Baugruppenträger BGT)

The 19” main frames include one MIL-1553B interface card FG380.122 each, as well as a triple switching power supply. The main frames can be equipped with up to 8 modules connected via a backplane. By this means each input signal, starting from port 2, is connected to the down-counter of module n and the up-counter of module n+1. Lemo connectors for the analog input (9xLEMO 2 pin), a differential analog output for the transmission of the last signal to the next main frame (LEMO 2 pin), calibration potis (9 pcs.), the sum interlock output and a gate-pulse input (2xLEMO 1 pin) are located on the backside.

Precise gain calibration of each channel is performed by dedicated trimpots mounted on the backpanel of each crate.

Branched or merged beamlines require special configurations of BCT pairs. The mapping of these structures is done by hard-wiring on the backplanes.

The 9th slot in the BGT is

At present 4 SVÜ main frames are installed.

Sections UN and EH are not monitored by the FBLC, yet.

It is not foreseen to monitor sections UL and UR.

## MIL-1553B Interfacekarte FG380.122 / FG380.211

An I/O-Bus IFK FG380.122 is used (end-of-life component), or the FG380.211 with I/O-Bus Piggy FG380.721 (both discontinued) for newer installations. The latter has been removed again, due to unsolved bus error problems.

## Interlock Status Display

The interlock status signals are displayed in HKR console 16. For online beam loss control 3 yellow LEDs are located in the column ‘Strahlverlust’ for sections UH, UA/UE and TK, giving a sum activity display for the related section. At the lower left a yellow LED named ‘Pulsverkürzung f. DG’ indicates if the macropulse is additionally dynamically truncated while the ‘PG-Schutz’ mode is switched on.

The actual sources of the interlock signals of the SVÜ are indicated by the red LEDs of the module ‘Strahlalarm’ in LSB 6 Rack 13, as well as LSB 4 Rack 14 (module ‘OUT50’).

Figure 4 Interlock Status Display in HKR

## Chopper Control System(CCS)

The CCS collects the various interlock signals, checks their relevancy with respect to the present state of the accelerator, and sends the control signals to the beam

chopper(s). The dynamic truncation action starts at 100 μs beam pulse length, and is limited to 10 μs, which is the shortest useful value for beam diagnostic instruments like profile grids, BCTs or Faraday-cups. The counting pulses are gated by appropriate timing signals (measurement gate and clamp pulses) in order to exclude erroneous counts from electromagnetic disturbances during the pulse gaps. The CCS provides dedicated gate pulses for each of the UNILAC timing zones, while keeping the macropulse always enclosed by the gate; the clamp pulses imbed the gates with 50µs advance and ~20 µs lag.

# Interfaces

## Input parameters / set values

- TODO: which input parameters have to be set? E.g. threshold values for beam loss... -> see ‘Gerätemodell’

## Hardware interfaces

The following sections present a complete list of HW interfaces of the three SVÜ board types SV, PGS and EMI.

### Hardware interfaces type SV

| Board Type SV - I/O-Signals |  |  |
| --- | --- | --- |
| Input Signals | Description | Tap |
| Analog channel 1 | Analog signal BCT#1 | Lemo 2p, backside |
| Analog channel 2 | Analog signal BCT#2 | Lemo 2p, backside |
| Beam loss threshold | Digital, from SE | VG backplane |
| Protection threshold | (not used with type SV) |  |
| Gate pulse | clamp pulse from chopper control system | Lemo 1p, backside |
| Output Signals | Description | Tap |
| Beam loss interlock signal | Digital, to chopper ctrl | VG backplane |
| Counter value | Digital, to SE | MIL-Bus |
| ILK- and SEQ-status | Digital, to SE | MIL-Bus |

Table 2

### Hardware interfaces type PGS

| Board Type PGS I/O-Signals |  |  |
| --- | --- | --- |
| Input Signals | Description | Tap |
| Analog channel 1 | Analog signal BCT#1 | Lemo 2p, backside |
| Analog channel 2 | Analog signal BCT#2 | Lemo 2p, backside |
| Beam loss threshold | Digital, from SE | VG backplane |
| Protection threshold | Digital, from SE | VG backplane |
| Gate pulse | clamp pulse from chopper control system | Lemo 1p, backside |
| Output Signals | Description | Tap |
| Beam loss interlock signal | Digital, to chopper ctrl | VG backplane |
| Counter value | Digital, to SE | MIL-Bus |
| ILK- and SEQ-status | Digital, to SE | MIL-Bus |

Table 3

### Hardware interfaces type EMI

| Board Type EMI I/O-Signals |  |  |
| --- | --- | --- |
| Input Signals | Description | Tap |
| Analog channel 1 | Analog signal BCT#1 | Lemo 2p, backside |
| Analog channel 2 | Analog signal BCT#2 | Lemo 2p, backside |
| Beam loss threshold | Digital, from SE | VG backplane |
| Protection threshold | Digital, from SE | VG backplane |
| Gate pulse | clamp pulse from chopper control system | Lemo 1p, backside |
| Output Signals | Description | Tap |
| Beam loss interlock signal | Digital, to chopper ctrl | VG backplane |
| Counter value | Digital, to SE | MIL-Bus |
| ILK- and SEQ-status | Digital, to SE | MIL-Bus |

Table 4

## Software interfaces

- The FBLC system is controlled by the IPD (Init Planungs-/Darstellungs-Programm) program. A detailed online-display of measured losses/beam charges and interlock stati was possible running “DTTC” under NODAL/OpenVMS on AXP machines. This is now obsolete, was replaced by “DEV-DTTC-INL”, written in Python/LINUX and running on ASL computers.

# Summary and Evaluation of the SVÜ

## Operational experience with FBLC

## Service and maintenance aspects

# Future Requirements

## Upgrades due to known SVÜ drawbacks

## General modernization aspects

## Upgrades due to FAIR requirements

## Merging with BCT DAQ and MAPS systems?

# Outlook

# Related Documents

[1]	P. Gerhard, J. Glatz, P. Kainberger, W. Panschow, S. Rauch, M. Rebscher, H. Reeg, N. Schneider, “Schnelle Strahlverlust-Überwachung für UNILAC, TK und EH”, GSI Technical Note, Darmstadt, 2006.

[2]	H. Reeg, J. Glatz, N. Schneider, H. Walter, “Machine Protection by active Current-Transmission Control at GSI-UNILAC”, TUPCH014, Proc. EPAC2006, Edinburgh, Scotland, 2006, pp. 1025.

[3]	P. Forck, “Lecture Notes on Beam Instrumentation and Diagnostics”, Joint University Accelerator School Gesellschaft für Schwerionenforschung (GSI) Darmstadt, Germany, January – March 2011

http://www-bd.gsi.de/conf/juas/juas_script.pdf

[4]	P. Kainberger, “DTTC – Strahlverlustüberwachung - Gerätemodell und Softwareentwurf”, Gesellschaft für Schwerionenforschung (GSI) Darmstadt, Germany, November 2003

http://bel.gsi.de/mk/dttc/gm_dttc.html

[5]	other

[6]	document.

# Abbreviations

| Akronym | Description |
| --- | --- |
| BCT | Beam Current Transformer |
| CPLD | Complex Programmable Logic Device |
| EH | Experimental hall |
| FBLC | Fast Beam Loss Control |
| HKR | Main control room (Hauptkontrollraum) |
| IFK | MILBus Interface card (Interface-Karte) |
| LSB | Local control area (Lokaler Steuer-Bereich) |
| MAPS | Macro Pulse Selector |
| SVÜ | Beam loss control (Strahlverlust-Überwachung) |
| TK | Transfer channel (Transfer-Kanal) |
| UNILAC | Univeral Linear Accelerator |